Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Equipment labels.

Warning signs and labels.

Pipe labels.

Duct labels.

Stencils.

Valve tags.

Warning tags.

ACTION SUBMITTALS

Product Data:  For each type of product indicated.

Equipment Label Schedule:  Include a listing of all equipment to be labeled with the proposed content for each label.

Valve numbering scheme.

Valve Schedules:  For each piping system to include in maintenance manuals.

COORDINATION

Coordinate installation of identifying devices with completion of covering and painting of surfaces where devices are to be applied.

Coordinate installation of identifying devices with locations of access panels and doors.

Install identifying devices before installing acoustical ceilings and similar concealment.

PRODUCTS

EQUIPMENT LABELS

Plastic Labels for Equipment:

Material and Thickness:  Multilayer, multicolor, plastic labels for mechanical engraving, 1/8 inch thick, and having predrilled holes for attachment hardware.

Letter Color:  White.

Background Color:  Black.

Maximum Temperature:  Able to withstand temperatures up to 160 deg F.

Minimum Label Size:  Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch.

Minimum Letter Size:  1/4 inch for name of units if viewing distance is less than 24 inches, 1/2 inch for viewing distances up to 72 inches, and proportionately larger lettering for greater viewing distances.  Include secondary lettering two-thirds to three-fourths the size of principal lettering.

Fasteners:  Stainless-steel self-tapping screws.

Adhesive:  Contact-type permanent adhesive, compatible with label and with substrate.

In first paragraph below, describe required label content.  The objective of labeling equipment is to coordinate it with Drawings, including plans, details, and schedules.  This will allow other information, such as capacities and operating characteristics, to be obtained.

Label Content:  Include equipment's unique equipment number.

Equipment Label Schedule:  For each item of equipment to be labeled, on 8-1/2-by-11-inch bond paper.  Tabulate equipment identification number, manufacturer, model number, and identify Drawing numbers where equipment is indicated (plans, details, and schedules), plus the Specification Section number and title where equipment is specified.  Equipment schedule shall be included in operation and maintenance data.

WARNING SIGNS AND LABELS

Material and Thickness:  Multilayer, multicolor, plastic labels for mechanical engraving, 1/8 inch thick, and having predrilled holes for attachment hardware.

Letter Color:  Black.

Background Color:  Yellow.

Maximum Temperature:  Able to withstand temperatures up to 160 deg F.

Minimum Label Size:  Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch.

Minimum Letter Size:  1/4 inch for name of units if viewing distance is less than 24 inches, 1/2 inch for viewing distances up to 72 inches, and proportionately larger lettering for greater viewing distances.  Include secondary lettering two-thirds to three-fourths the size of principal lettering.

Fasteners:  Stainless-steel rivets or self-tapping screws.

Adhesive:  Contact-type permanent adhesive, compatible with label and with substrate.

In paragraph below, describe required label content.  The objective of labeling equipment is to coordinate it with Drawings, including plans, details, and schedules.  This will allow other information, such as capacities and operating characteristics, to be obtained.

Label Content:  Include caution and warning information, plus emergency notification instructions.

PIPE LABELS

Retain this article if these devices will identify some or all piping.  Identification of piping by color-coded painting is covered in "Pipe Label Installation" Article.

Do not use pipe labels or plastic tapes for bare pipes conveying fluids at temperatures of 125 deg F (52 deg C) or higher.

General Requirements for Manufactured Pipe Labels:  Preprinted, color-coded, with lettering indicating service, and showing flow direction.

Pretensioned Pipe Labels:  Precoiled, semirigid plastic formed to cover full circumference of pipe and to attach to pipe without fasteners or adhesive.

Pipe Label Contents:  Include identification of piping service using same designations or abbreviations as used on Drawings, pipe size, and an arrow indicating flow direction.

Flow-Direction Arrows:  Integral with piping system service lettering to accommodate both directions, or as separate unit on each pipe label to indicate flow direction.

Lettering Size:  At least 1-1/2 incheshigh.

DUCT LABELS

Material and Thickness:  Multilayer, multicolor, plastic labels for mechanical engraving, 1/8 inch thick, and having predrilled holes for attachment hardware.

Maximum Temperature:  Able to withstand temperatures up to 160 deg F.

Minimum Label Size:  Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch.

Minimum Letter Size:  1/4 inch for name of units if viewing distance is less than 24 inches, 1/2 inch for viewing distances up to 72 inches, and proportionately larger lettering for greater viewing distances.  Include secondary lettering two-thirds to three-fourths the size of principal lettering.

Adhesive:  Contact-type permanent adhesive, compatible with label and with substrate.

Duct Label Contents:  Include identification of duct service using same designations or abbreviations as used on Drawings, duct size, and an arrow indicating flow direction.

Flow-Direction Arrows:  Integral with duct system service lettering to accommodate both directions, or as separate unit on each duct label to indicate flow direction.

Lettering Size:  At least 1-1/2 inches high.

VALVE TAGS

Retain requirement in "Action Submittals" Article to submit numbering scheme for approval.

Valve Tags:  Stamped or engraved with 1/4-inch letters for piping system abbreviation and 1/2-inch numbers.

Tag Material:  Brass, 0.032-inch minimum thickness, and having predrilled or stamped holes for attachment hardware.

Fasteners:  Brass wire-link or beaded chain; or S-hook.

Valve Schedules:  For each piping system, on 8-1/2-by-11-inch bond paper.  Tabulate valve number, piping system, system abbreviation (as shown on valve tag), location of valve (room or space), normal-operating position (open, closed, or modulating), and variations for identification.  Mark valves for emergency shutoff and similar special uses.

Valve-tag schedule shall be included in operation and maintenance data.

WARNING TAGS

Warning Tags:  Preprinted or partially preprinted, accident-prevention tags, of plasticized card stock with matte finish suitable for writing.

Size:  3 by 5-1/4 inches minimum.

Fasteners:  Brass grommet and wire.

Nomenclature:  Large-size primary caption such as "DANGER," "CAUTION," or "DO NOT OPERATE."

Color:  Yellow background with black lettering.

EXECUTION

PREPARATION

Clean piping and equipment surfaces of substances that could impair bond of identification devices, including dirt, oil, grease, release agents, and incompatible primers, paints, and encapsulants.

EQUIPMENT LABEL INSTALLATION

Install or permanently fasten labels on each major item of mechanical equipment.

Locate equipment labels where accessible and visible.

PIPE LABEL INSTALLATION

Retain first paragraph below to identify piping systems by color-coded painting.  Labels will still be required to identify service, pipe size, and flow direction.

Piping Color-Coding:  Painting of piping is specified in other sections.

Retain first paragraph below only if stenciled labels are permitted.

Revise first paragraph below to suit Project.

Locate pipe labels where piping is exposed or above accessible ceilings in finished spaces; machine rooms; accessible maintenance spaces such as shafts, tunnels, and plenums; and exterior exposed locations as follows:

Near each valve and control device.

Near each branch connection, excluding short takeoffs for fixtures and terminal units.  Where flow pattern is not obvious, mark each pipe at branch.

Near penetrations through walls, floors, ceilings, and inaccessible enclosures.

At access doors, manholes, and similar access points that permit view of concealed piping.

Near major equipment items and other points of origination and termination.

Spaced at maximum intervals of 50 feet along each run.  Reduce intervals to 25 feet in areas of congested piping and equipment.

On piping above removable acoustical ceilings.  Omit intermediately spaced labels.

Pipe Label Color Schedule:

Chilled-Water Piping:

Background Color:  Blue.

Letter Color:  White.

Letter Color:  Black.

Refrigerant Piping:

Background Color:  Orange.

Letter Color:  Black.

DUCT LABEL INSTALLATION

Install plastic-laminated duct labels with permanent adhesive on air ducts in the following color codes:

Blue: For cold-air supply ducts.

Yellow:  For hot-air supply ducts.

Green:  For exhaust-, outside-, relief-, return-, and mixed-air ducts.

ASME A13.1 Colors and Designs:  For hazardous material exhaust.

Retain first paragraph below only if stenciled labels are permitted.

Locate labels near points where ducts enter into concealed spaces and at maximum intervals of 50 feet in each space where ducts are exposed or concealed by removable ceiling system.

VALVE-TAG INSTALLATION

Revise this article as required to delete an entire piping system from tagging or other changes.  A schedule is helpful for complex projects.  Retain and revise first paragraph below if a schedule is prepared.

Install tags on valves and control devices in piping systems, except check valves; valves within factory-fabricated equipment units; shutoff valves; faucets; convenience and lawn-watering hose connections; and HVAC terminal devices and similar roughing-in connections of end-use fixtures and units.  List tagged valves in a valve schedule.

Valve-Tag Application Schedule:  Tag valves according to size, shape, and color scheme and with captions similar to those indicated in the following subparagraphs:

Other valve-tag sizes, shapes, colors, and letter colors may be available if required.

Valve-Tag Size and Shape:

All Valve-Tags:  1-1/2 inches minimum, round.

Select contrasting valve-tag color and letter color in two subparagraphs below for each service.  Retain "Natural" option for brass or stainless-steel valve tags.

Valve-Tag Color:

All Valve-Tags:  Natural.

Letter Color:

All Valve-Tags: Black.

WARNING-TAG INSTALLATION

Write required message on, and attach warning tags to, equipment and other items where required.

END OF SECTION 230553