# M&P Specification Review Report

Generated: 2025-12-10 13:07
Model: claude-sonnet-4-5-20250929
Files Reviewed: 5

# Files Reviewed

230529 - HANGERS AND SUPPORTS.docx

230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

230713 - DUCT INSULATION.docx

230719 - HVAC PIPING INSULATION.docx

# Summary

| CRITICAL 3 | HIGH 4 | MEDIUM 24 | LOW 5 | GRIPES 2 | TOTAL 38 |
| --- | --- | --- | --- | --- | --- |

Token Usage: 44,775 input → 8,542 output

Processing Time: 127.5 seconds

# Alerts

## LEED References Detected

The following LEED references were found. Since this is not a LEED project, these should be removed:

230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Line 49: LEED

Line 121: LEED

Line 125: LEED

Line 217: LEED

230713 - DUCT INSULATION.docx

Line 59: LEED

Line 61: LEED

Line 65: LEED

Line 261: LEED

Line 265: LEED

... and 7 more

230719 - HVAC PIPING INSULATION.docx

Line 45: LEED

Line 47: LEED

Line 51: LEED

Line 233: LEED

Line 237: LEED

... and 11 more

# Findings

# CRITICAL (3)

1. [CRITICAL] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 1, Article 1.4 - Performance Requirements

Issue: References ASCE/SEI 7 without specifying the required edition (ASCE 7-22 as adopted by CBC 2022). DSA requires compliance with the current adopted code edition for seismic design of hangers and supports.

Action: EDIT

Existing Text: Structural Performance: Hangers and supports for HVAC piping and equipment shall withstand the effects of gravity loads and stresses within limits and under conditions indicated according to ASCE/SEI 7.

Replace With: Structural Performance: Hangers and supports for HVAC piping and equipment shall withstand the effects of gravity loads and stresses within limits and under conditions indicated according to ASCE/SEI 7-22 as adopted by CBC 2022.

Reference: CBC 2022 Chapter 16

2. [CRITICAL] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 1, Article 1.4 - Performance Requirements

Issue: Missing explicit requirement for DSA seismic certification and pre-approval documentation for hangers and supports. DSA IR A-6 requires seismic certification for nonstructural components.

Action: ADD

Replace With: Provide seismic certification documentation per DSA IR A-6 for all hangers, supports, and trapeze assemblies. Submit OSHPD pre-approval (OPA) documentation where applicable for proprietary seismic restraint systems.

Reference: DSA IR A-6

3. [CRITICAL] 230713 - DUCT INSULATION.docx

Section: Part 3, Article 3.10 - Indoor Duct and Plenum Insulation Schedule

Issue: Kitchen hood exhaust duct fire rating requirement does not reference California Mechanical Code requirements for Type I hood exhaust systems, which may require different ratings based on specific conditions.

Action: EDIT

Existing Text: Concealed, Type I, Commercial, Kitchen Hood Exhaust Duct and Plenum Insulation: Fire-rated blanket or board; thickness as required to achieve 2-hour fire rating.

Replace With: Concealed, Type I, Commercial, Kitchen Hood Exhaust Duct and Plenum Insulation: Fire-rated blanket or board; thickness as required to achieve fire rating per CMC 2022 Section 506.3.13 and as indicated on Drawings. Verify required rating with Authority Having Jurisdiction.

Reference: CMC 2022 Section 506.3.13

# HIGH (4)

1. [HIGH] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 1, Article 1.6 - Action Submittals

Issue: Shop drawings requiring Professional Engineer seal and signature lack explicit requirement for California PE licensure, which is required for DSA projects.

Action: EDIT

Existing Text: Shop Drawings: Signed and sealed by a qualified professional engineer.

Replace With: Shop Drawings: Signed and sealed by a professional engineer licensed in the State of California.

Reference: California Business and Professions Code Section 6700 et seq.

2. [HIGH] 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 2, Article 2.5 - Valve Tags

Issue: Specification lacks requirement for seismic shutoff valve identification, which is required for gas piping systems in California K-12 facilities per DSA requirements.

Action: ADD

Replace With: Seismic Gas Shutoff Valves: Provide distinctive tags or labels clearly identifying seismic gas shutoff valves with the words "SEISMIC GAS SHUTOFF VALVE" in letters at least 1/2 inch high. Include location and instructions for manual reset if applicable.

Reference: California Government Code Section 8875.7, DSA IR A-18

3. [HIGH] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, Article 1.5 - Action Submittals

Issue: References ASHRAE 62.1 and ASHRAE/IESNA 90.1 without specifying required editions. California Energy Code and DSA require specific editions for compliance verification.

Action: EDIT

Existing Text: Air-Balance Report for Prerequisite IEQ 1: Documentation of work performed for ASHRAE 62.1, Section 7.2.2 - "Air Balancing."
TAB Report for Prerequisite EA 2: Documentation of work performed for ASHRAE/IESNA 90.1, Section 6.7.2.3 - "System Balancing."

Replace With: Air-Balance Report: Documentation of work performed per ASHRAE 62.1-2022, Section 7.2.2 - "Air Balancing."
TAB Report: Documentation of work performed per ASHRAE/IES 90.1-2019 as adopted by California Energy Code (Title 24, Part 6), Section 120.6 - "Mandatory Requirements for Ventilation and Indoor Air Quality" and Section 140.4 - "Prescriptive Requirements for Space Conditioning Systems."

Reference: California Energy Code (Title 24, Part 6) 2022

4. [HIGH] 230713 - DUCT INSULATION.docx

Section: Part 2, Article 2.7 - Factory-Applied Jackets

Issue: References ASTM C 1136 without year designation and does not specify Type clearly enough. Current standard is ASTM C1136-22.

Action: EDIT

Existing Text: FSK Jacket: Aluminum-foil, fiberglass-reinforced scrim with kraft-paper backing; complying with ASTM C 1136, Type II.

Replace With: FSK Jacket: Aluminum-foil, fiberglass-reinforced scrim with kraft-paper backing; complying with ASTM C1136-22, Type II.

# MEDIUM (24)

1. [MEDIUM] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 2, Article 2.5 - Thermal-Hanger Shield Inserts

Issue: References ASTM C 533 without year designation. Current standard is ASTM C533-20.

Action: EDIT

Existing Text: Insulation-Insert Material for Cold Piping: Water-repellent treated, ASTM C 533, Type I calcium silicate with 100-psig minimum compressive strength.
Insulation-Insert Material for Hot Piping: Water-repellent treated, ASTM C 533, Type I calcium silicate with 100-psig minimum compressive strength.

Replace With: Insulation-Insert Material for Cold Piping: Water-repellent treated, ASTM C533-20, Type I calcium silicate with 100-psig minimum compressive strength.
Insulation-Insert Material for Hot Piping: Water-repellent treated, ASTM C533-20, Type I calcium silicate with 100-psig minimum compressive strength.

2. [MEDIUM] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 2, Article 2.9 - Miscellaneous Materials

Issue: References ASTM A 36/A 36M without year designation. Current standard is ASTM A36/A36M-19.

Action: EDIT

Existing Text: Structural Steel: ASTM A 36/A 36M, carbon-steel plates, shapes, and bars; black and galvanized.

Replace With: Structural Steel: ASTM A36/A36M-19, carbon-steel plates, shapes, and bars; black and galvanized.

3. [MEDIUM] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 2, Article 2.9 - Miscellaneous Materials

Issue: References ASTM C 1107 without year designation. Current standard is ASTM C1107/C1107M-20.

Action: EDIT

Existing Text: Grout: ASTM C 1107, factory-mixed and -packaged, dry, hydraulic-cement, nonshrink and nonmetallic grout

Replace With: Grout: ASTM C1107/C1107M-20, factory-mixed and -packaged, dry, hydraulic-cement, nonshrink and nonmetallic grout

4. [MEDIUM] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 3, Article 3.2 - Hanger and Support Installation

Issue: References outdated section number for roof accessories. Current CSI MasterFormat uses Division 07 75 00 for Roof Specialties and Accessories.

Action: EDIT

Existing Text: Curb-Mounted-Type Pipe Stands: Assemble components or fabricate pipe stand and mount on permanent, stationary roof curb. See Section 077200 "Roof Accessories" for curbs.

Replace With: Curb-Mounted-Type Pipe Stands: Assemble components or fabricate pipe stand and mount on permanent, stationary roof curb. See Section 077500 "Roof Specialties and Accessories" for curbs.

5. [MEDIUM] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 3, Article 3.4 - Painting

Issue: References ASTM A 780 without year designation. Current standard is ASTM A780/A780M-19.

Action: EDIT

Existing Text: Galvanized Surfaces: Clean welds, bolted connections, and abraded areas and apply galvanizing-repair paint to comply with ASTM A 780.

Replace With: Galvanized Surfaces: Clean welds, bolted connections, and abraded areas and apply galvanizing-repair paint to comply with ASTM A780/A780M-19.

6. [MEDIUM] 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 2, Article 2.4 - Duct Labels

Issue: References ASTM E 84 surface burning characteristics, but the standard designation should include the year. Current standard is ASTM E84-22a.

Action: EDIT

Existing Text: Material and Thickness: Multilayer, multicolor, plastic labels for mechanical engraving, 1/8 inch thick

Replace With: Material and Thickness: Multilayer, multicolor, plastic labels for mechanical engraving, 1/8 inch thick, with surface burning characteristics per ASTM E84-22a suitable for the application

7. [MEDIUM] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, Article 1.8 - Quality Assurance

Issue: References ASHRAE 111 without year designation. Current standard is ASHRAE 111-2022.

Action: EDIT

Existing Text: Instrumentation Type, Quantity, Accuracy, and Calibration: As described in ASHRAE 111, Section 5, "Instrumentation."

Replace With: Instrumentation Type, Quantity, Accuracy, and Calibration: As described in ASHRAE 111-2022, Section 5, "Instrumentation."

8. [MEDIUM] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, Article 1.8 - Quality Assurance

Issue: References ASHRAE 62.1 and ASHRAE/IESNA 90.1 without year designations, applies throughout the specification.

Action: EDIT

Existing Text: ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 7.2.2 - "Air Balancing."
ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6.7.2.3 - "System Balancing."

Replace With: ASHRAE Compliance: Applicable requirements in ASHRAE 62.1-2022, Section 7.2.2 - "Air Balancing."
ASHRAE/IES Compliance: Applicable requirements in ASHRAE/IES 90.1-2019 as adopted by California Energy Code, Section 6.7.2.3 - "System Balancing."

9. [MEDIUM] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 3, Article 3.3 - General Procedures for Testing and Balancing

Issue: References SMACNA's "HVAC Systems - Testing, Adjusting, and Balancing" without edition year. Current edition should be specified.

Action: EDIT

Existing Text: Perform testing and balancing procedures on each system according to the procedures contained in AABC's "National Standards for Total System Balance", ASHRAE 111, and SMACNA's "HVAC Systems - Testing, Adjusting, and Balancing"

Replace With: Perform testing and balancing procedures on each system according to the procedures contained in AABC's "National Standards for Total System Balance" (current edition), ASHRAE 111-2022, and SMACNA's "HVAC Systems - Testing, Adjusting, and Balancing" (4th Edition, 2021)

10. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 1, Article 1.7 - Quality Assurance

Issue: References ASTM E 84 without year designation, applies throughout this section. Current standard is ASTM E84-22a.

Action: EDIT

Existing Text: Surface-Burning Characteristics: For insulation and related materials, as determined by testing identical products according to ASTM E 84

Replace With: Surface-Burning Characteristics: For insulation and related materials, as determined by testing identical products according to ASTM E84-22a

11. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 2, Article 2.1 - Insulation Materials

Issue: References multiple ASTM standards without year designations including ASTM C 553, C 1290, C 612, C 1393, and C 656, applies throughout the insulation materials article.

Action: EDIT

Existing Text: Mineral-Fiber Blanket Insulation: Mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C 553, Type II and ASTM C 1290, Type III

Replace With: Mineral-Fiber Blanket Insulation: Mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C553-20, Type II and ASTM C1290-21, Type III

12. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 2, Article 2.4 - Mastics

Issue: References MIL-PRF-19565C without stating it is a military specification that may not be current. Consider whether commercial standards are more appropriate for California K-12 projects.

Action: EDIT

Existing Text: Materials shall be compatible with insulation materials, jackets, and substrates; comply with MIL-PRF-19565C, Type II.

Replace With: Materials shall be compatible with insulation materials, jackets, and substrates. For vapor-barrier mastics, comply with ASTM C1136-22, Type I (vapor-retarder) or equivalent military specification MIL-PRF-19565C, Type II.

13. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 2, Article 2.8 - Field-Applied Jackets

Issue: References ASTM C 921, ASTM B 209 without year designations.

Action: EDIT

Existing Text: Field-applied jackets shall comply with ASTM C 921, Type I, unless otherwise indicated.
...
Aluminum Jacket: Comply with ASTM B 209, Alloy 3003, 3005, 3105, or 5005, Temper H-14.

Replace With: Field-applied jackets shall comply with ASTM C921-22, Type I, unless otherwise indicated.
...
Aluminum Jacket: Comply with ASTM B209-14(2019), Alloy 3003, 3005, 3105, or 5005, Temper H-14.

14. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 2, Article 2.9 - Tapes

Issue: References ASTM C 1136 without year designation for FSK tape.

Action: EDIT

Existing Text: FSK Tape: Foil-face, vapor-retarder tape matching factory-applied jacket with acrylic adhesive; complying with ASTM C 1136.

Replace With: FSK Tape: Foil-face, vapor-retarder tape matching factory-applied jacket with acrylic adhesive; complying with ASTM C1136-22.

15. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 3, Article 3.7 - Fire-Rated Insulation System Installation

Issue: References Section 078413 "Penetration Firestopping" which uses outdated CSI section numbering. Current format is typically 078400 series.

Action: EDIT

Existing Text: Install firestopping at penetrations through fire-rated assemblies. Fire-stop systems are specified in Section 078413 "Penetration Firestopping."

Replace With: Install firestopping at penetrations through fire-rated assemblies. Fire-stop systems are specified in Section 078400 "Fire and Smoke Protection" or applicable firestopping section.

16. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 1, Article 1.7 - Quality Assurance

Issue: References ASTM E 84 without year designation. Current standard is ASTM E84-22a.

Action: EDIT

Existing Text: Surface-Burning Characteristics: For insulation and related materials, as determined by testing identical products according to ASTM E 84

Replace With: Surface-Burning Characteristics: For insulation and related materials, as determined by testing identical products according to ASTM E84-22a

17. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 2, Article 2.1 - Insulation Materials

Issue: References ASTM C 534, C 547, C 1393, and C 612 without year designations, applies throughout the insulation materials article.

Action: EDIT

Existing Text: Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C 534, Type I for tubular materials.

Replace With: Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C534-20, Type I for tubular materials.

18. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 2, Article 2.2 - Insulating Cements

Issue: References ASTM C 195 without year designation. Current standard is ASTM C195-20.

Action: EDIT

Existing Text: Mineral-Fiber Insulating Cement: Comply with ASTM C 195.

Replace With: Mineral-Fiber Insulating Cement: Comply with ASTM C195-20.

19. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 2, Article 2.3 - Adhesives

Issue: References MIL-A-24179A and MIL-A-3316C without noting these are military specifications that may not be current or may have commercial equivalents.

Action: EDIT

Existing Text: Flexible Elastomeric and Polyolefin Adhesive: Comply with MIL-A-24179A, Type II, Class I.

Replace With: Flexible Elastomeric and Polyolefin Adhesive: Comply with MIL-A-24179A, Type II, Class I, or equivalent commercial specification meeting the same performance requirements.

20. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 2, Article 2.4 - Mastics

Issue: References ASTM E 96/E 96M and ASTM F 1249 without year designations.

Action: EDIT

Existing Text: Water-Vapor Permeance: ASTM E 96/E 96M, Procedure B, 0.013 perm at 43-mil dry film thickness.
...
Water-Vapor Permeance: ASTM F 1249, 1.8 perms at 0.0625-inch dry film thickness.

Replace With: Water-Vapor Permeance: ASTM E96/E96M-22, Procedure B, 0.013 perm at 43-mil dry film thickness.
...
Water-Vapor Permeance: ASTM F1249-20, 1.8 perms at 0.0625-inch dry film thickness.

21. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 2, Article 2.7 - Factory-Applied Jackets

Issue: References ASTM C 1136 without year designation.

Action: EDIT

Existing Text: ASJ: White, kraft-paper, fiberglass-reinforced scrim with aluminum-foil backing; complying with ASTM C 1136, Type I.
FSK Jacket: Aluminum-foil, fiberglass-reinforced scrim with kraft-paper backing; complying with ASTM C 1136, Type II.

Replace With: ASJ: White, kraft-paper, fiberglass-reinforced scrim with aluminum-foil backing; complying with ASTM C1136-22, Type I.
FSK Jacket: Aluminum-foil, fiberglass-reinforced scrim with kraft-paper backing; complying with ASTM C1136-22, Type II.

22. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 2, Article 2.8 - Field-Applied Jackets

Issue: References ASTM C 921 and ASTM B 209 without year designations.

Action: EDIT

Existing Text: Field-applied jackets shall comply with ASTM C 921, Type I, unless otherwise indicated.
...
Aluminum Jacket: Comply with ASTM B 209, Alloy 3003, 3005, 3105, or 5005, Temper H-14.

Replace With: Field-applied jackets shall comply with ASTM C921-22, Type I, unless otherwise indicated.
...
Aluminum Jacket: Comply with ASTM B209-14(2019), Alloy 3003, 3005, 3105, or 5005, Temper H-14.

23. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 3, Article 3.3 - Penetrations

Issue: References Section 078413 "Penetration Firestopping" which uses outdated CSI section numbering, applies throughout the penetrations article.

Action: EDIT

Existing Text: Comply with requirements in Section 078413 "Penetration Firestopping" for firestopping and fire-resistive joint sealers.

Replace With: Comply with requirements in Section 078400 "Fire and Smoke Protection" or applicable firestopping section for firestopping and fire-resistive joint sealers.

24. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 3, Article 3.8 - Finishes

Issue: References Section 099113 and Section 099123 which use outdated CSI section numbering format.

Action: EDIT

Existing Text: Pipe Insulation with ASJ, Glass-Cloth, or Other Paintable Jacket Material: Paint jacket with paint system identified below and as specified in Section 099113 "Exterior Painting" and Section 099123 "Interior Painting."

Replace With: Pipe Insulation with ASJ, Glass-Cloth, or Other Paintable Jacket Material: Paint jacket with paint system identified below and as specified in Section 099000 "Finishes" painting sections or as applicable.

# LOW (5)

1. [LOW] 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 3, Article 3.4 - Duct Label Installation

Issue: Inconsistent specification of label spacing intervals. The text states '50 feet' for maximum intervals but does not address DSA accessibility requirements for labels in areas above accessible ceilings.

Action: EDIT

Existing Text: Locate labels near points where ducts enter into concealed spaces and at maximum intervals of 50 feet in each space where ducts are exposed or concealed by removable ceiling system.

Replace With: Locate labels near points where ducts enter into concealed spaces and at maximum intervals of 50 feet in each space where ducts are exposed or concealed by removable ceiling system. Ensure labels in accessible ceiling spaces are visible from access points.

2. [LOW] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 3, Article 3.3 - General Procedures for Testing and Balancing

Issue: References Section 230713, 230716, and 230719 for insulation restoration but uses outdated section numbering format.

Action: EDIT

Existing Text: Restore insulation, coverings, vapor barrier, and finish according to Section 230713 "Duct Insulation," Section 230716 "HVAC Equipment Insulation," and Section 230719 "HVAC Piping Insulation."

Replace With: Restore insulation, coverings, vapor barrier, and finish according to Section 230700 "HVAC Insulation" or individual insulation sections as applicable.

3. [LOW] 230529 - HANGERS AND SUPPORTS.docx

Section: Throughout specification

Issue: Inconsistent use of spacing in ASTM designations (e.g., 'ASTM A 36' vs 'ASTM A36'). Standard format per ASTM is without space.

Action: EDIT

Existing Text: ASTM A 36, ASTM C 533, etc.

Replace With: ASTM A36, ASTM C533, etc.

4. [LOW] 230713 - DUCT INSULATION.docx

Section: Throughout specification

Issue: Inconsistent use of spacing in ASTM designations throughout the specification (e.g., 'ASTM C 553' vs 'ASTM C553').

Action: EDIT

Existing Text: Various instances of ASTM designations with spaces

Replace With: Remove spaces from ASTM designations throughout for consistency (e.g., ASTM C553, ASTM C1290)

5. [LOW] 230719 - HVAC PIPING INSULATION.docx

Section: Throughout specification

Issue: Inconsistent use of spacing in ASTM designations throughout the specification.

Action: EDIT

Existing Text: Various instances of ASTM designations with spaces

Replace With: Remove spaces from ASTM designations throughout for consistency

# GRIPES (2)

1. [GRIPES] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 3, Article 3.5 - Hanger and Support Schedule

Issue: The schedule lists 30+ different MSS hanger types with detailed specifications. For a K-12 project, this level of granularity may be excessive and could lead to coordination issues. Consider consolidating to the most commonly used types (Types 1, 2, 4, 36, 38, and 41) and allowing contractor to select appropriate types from MSS SP-58 for other applications. This would reduce specification bulk while maintaining quality.

Action: EDIT

2. [GRIPES] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, Article 1.8 - Quality Assurance

Issue: Requiring AABC certification for TAB contractor, field supervisor, AND technicians may be unnecessarily restrictive for California K-12 projects and could limit the pool of qualified contractors, potentially increasing costs. NEBB or TABB certifications are equally valid. Consider allowing 'AABC, NEBB, or TABB certification' instead.

Action: EDIT