# M&P Specification Review Report

Generated: 2025-12-10 13:20
Model: claude-opus-4-5-20251101
Files Reviewed: 5

# Files Reviewed

230529 - HANGERS AND SUPPORTS.docx

230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

230713 - DUCT INSULATION.docx

230719 - HVAC PIPING INSULATION.docx

# Summary

| CRITICAL 4 | HIGH 7 | MEDIUM 10 | LOW 6 | GRIPES 2 | TOTAL 29 |
| --- | --- | --- | --- | --- | --- |

Token Usage: 44,805 input → 8,767 output

Processing Time: 145.7 seconds

# Alerts

## LEED References Detected

The following LEED references were found. Since this is not a LEED project, these should be removed:

230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Line 49: LEED

Line 121: LEED

Line 125: LEED

Line 217: LEED

230713 - DUCT INSULATION.docx

Line 59: LEED

Line 61: LEED

Line 65: LEED

Line 261: LEED

Line 265: LEED

... and 7 more

230719 - HVAC PIPING INSULATION.docx

Line 45: LEED

Line 47: LEED

Line 51: LEED

Line 233: LEED

Line 237: LEED

... and 11 more

# Findings

# CRITICAL (4)

1. [CRITICAL] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 1, Performance Requirements

Issue: Seismic design references generic 'ASCE/SEI 7' without specifying the edition required by CBC 2022. For DSA projects, must reference ASCE 7-22 as adopted by CBC 2022, and must include DSA IR A-6 seismic restraint requirements.

Action: EDIT

Existing Text: Structural Performance:  Hangers and supports for HVAC piping and equipment shall withstand the effects of gravity loads and stresses within limits and under conditions indicated according to ASCE/SEI 7.

Replace With: Structural Performance:  Hangers and supports for HVAC piping and equipment shall withstand the effects of gravity loads and stresses within limits and under conditions indicated according to ASCE 7-22 as adopted by CBC 2022. Seismic bracing shall comply with DSA IR A-6 and OSHPD pre-approval requirements where applicable.

Reference: CBC 2022 Chapter 16, DSA IR A-6

2. [CRITICAL] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 1, Action Submittals

Issue: Missing required DSA seismic certification submittal requirements. DSA projects require seismic restraint calculations and certifications per DSA IR A-6.

Action: ADD

Replace With: Seismic Restraint Submittals: Submit seismic restraint calculations and certification documentation per DSA IR A-6. Include OSHPD pre-approval (OPA) documentation for seismic bracing components where applicable. Calculations shall be signed and sealed by a California-licensed professional engineer.

Reference: DSA IR A-6

3. [CRITICAL] 230713 - DUCT INSULATION.docx

Section: Part 2, Insulation Materials

Issue: No reference to California Energy Code (Title 24, Part 6) insulation requirements. For California K-12 projects, duct insulation must comply with Title 24 minimum R-values which may exceed ASHRAE 90.1 requirements.

Action: ADD

Replace With: Comply with California Energy Code (Title 24, Part 6) minimum insulation R-values. Where Title 24 requirements exceed values specified herein, Title 24 shall govern.

Reference: California Title 24, Part 6

4. [CRITICAL] 230719 - HVAC PIPING INSULATION.docx

Section: Part 2, Insulation Materials

Issue: No reference to California Energy Code (Title 24, Part 6) pipe insulation requirements. California K-12 projects must comply with Title 24 Table 120.3-A minimum pipe insulation thicknesses.

Action: ADD

Replace With: Comply with California Energy Code (Title 24, Part 6) minimum pipe insulation thicknesses per Table 120.3-A. Where Title 24 requirements exceed values specified herein, Title 24 shall govern.

Reference: California Title 24, Part 6, Table 120.3-A

# HIGH (7)

1. [HIGH] 230713 - DUCT INSULATION.docx

Section: Part 2, Insulation Materials, Mineral-Fiber Blanket Insulation

Issue: References ASTM C 553 which was withdrawn in 2018. This standard is no longer valid and products certified to it may not be available.

Action: EDIT

Existing Text: Comply with ASTM C 553, Type II and ASTM C 1290, Type III with factory-applied FSK jacket.

Replace With: Comply with ASTM C1290, Type III with factory-applied FSK jacket.

Reference: ASTM C1290

2. [HIGH] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, Quality Assurance

Issue: Specifies only AABC certification for TAB contractor, excluding NEBB-certified contractors. This unnecessarily restricts competition and may limit qualified bidders. Both certifying organizations are industry-recognized equivalents.

Action: EDIT

Existing Text: TAB Contractor Qualifications:  Engage a TAB entity certified by AABC.

Replace With: TAB Contractor Qualifications:  Engage a TAB entity certified by AABC or NEBB.

3. [HIGH] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, Quality Assurance

Issue: References outdated 'ASHRAE/IESNA 90.1' nomenclature. IESNA was removed from the standard title in 2010. Current reference should be ASHRAE 90.1-2022 for CBC 2022 compliance.

Action: EDIT

Existing Text: ASHRAE/IESNA Compliance:  Applicable requirements in ASHRAE/IESNA 90.1, Section 6.7.2.3 - "System Balancing."

Replace With: ASHRAE Compliance:  Applicable requirements in ASHRAE 90.1, Section 6.7.2.3 - "System Balancing."

Reference: ASHRAE 90.1

4. [HIGH] 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 3, Pipe Label Installation, Pipe Label Color Schedule

Issue: Chilled-Water Piping has contradictory letter color specifications listing both 'White' and 'Black'. This will cause confusion during installation.

Action: EDIT

Existing Text: Chilled-Water Piping:

Background Color:  Blue.

Letter Color:  White.

Letter Color:  Black.

Replace With: Chilled-Water Piping:

Background Color:  Blue.

Letter Color:  White.

Reference: ASME A13.1

5. [HIGH] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 2, Pipe Stands, High-Type Single-Pipe Stand

Issue: Specifies cadmium-plated steel components. Cadmium is a toxic heavy metal with significant health and environmental concerns, and its use is increasingly restricted. Zinc or stainless steel alternatives should be specified.

Action: EDIT

Existing Text: Vertical Members:  Two or more cadmium-plated-steel or stainless-steel, continuous-thread rods.

Horizontal Member:  Cadmium-plated-steel or stainless-steel rod with plastic or stainless-steel, roller-type pipe support.

Replace With: Vertical Members:  Two or more hot-dip galvanized steel or stainless-steel, continuous-thread rods.

Horizontal Member:  Hot-dip galvanized steel or stainless-steel rod with plastic or stainless-steel, roller-type pipe support.

6. [HIGH] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 1, Quality Assurance

Issue: Pipe welding qualifications reference 'ASME Boiler and Pressure Vessel Code' which is overly broad for building services piping. Should reference ASME B31.9 for building services piping or appropriate section of ASME B31.

Action: EDIT

Existing Text: Pipe Welding Qualifications:  Qualify procedures and operators according to ASME Boiler and Pressure Vessel Code.

Replace With: Pipe Welding Qualifications:  Qualify procedures and personnel according to ASME B31.9 for building services piping, or applicable section of ASME B31 for the specific piping service.

Reference: ASME B31.9

7. [HIGH] 230719 - HVAC PIPING INSULATION.docx

Section: Part 3, Indoor Piping Insulation Schedule

Issue: Chilled water insulation specified as 1 inch thick mineral-fiber for all pipe sizes. Title 24 Part 6 Table 120.3-A requires varying thicknesses based on pipe size. For pipes larger than 1.5 inches, minimum 1.5 inch insulation is required.

Action: EDIT

Existing Text: Mineral-Fiber, Preformed Pipe, Type I:  1 inch thick.

Replace With: Mineral-Fiber, Preformed Pipe, Type I: NPS 1 and smaller: 1 inch thick; NPS 1-1/4 to NPS 4: 1-1/2 inches thick; NPS 5 and larger: 2 inches thick. Verify compliance with Title 24, Part 6, Table 120.3-A.

Reference: California Title 24, Part 6, Table 120.3-A

# MEDIUM (10)

1. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 2, Adhesives

Issue: References 'California Department of Health Services' which was reorganized. The current agency is California Department of Public Health (CDPH), and the referenced standard is now 'CDPH Standard Method v1.2'.

Action: EDIT

Existing Text: California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Replace With: California Department of Public Health (CDPH) Standard Method v1.2 for testing VOC emissions.

Reference: CDPH Standard Method v1.2

2. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 2, Adhesives

Issue: References outdated 'California Department of Health Services' standard. This applies throughout this specification section.

Action: EDIT

Existing Text: California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Replace With: California Department of Public Health (CDPH) Standard Method v1.2 for testing VOC emissions.

Reference: CDPH Standard Method v1.2

3. [MEDIUM] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 1, Quality Assurance

Issue: AWS D1.1/D1.1M referenced without year. For current code compliance, should reference AWS D1.1/D1.1M:2020 or later.

Action: EDIT

Existing Text: Structural Steel Welding Qualifications:  Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

Replace With: Structural Steel Welding Qualifications:  Qualify procedures and personnel according to AWS D1.1/D1.1M:2020, "Structural Welding Code - Steel."

Reference: AWS D1.1/D1.1M:2020

4. [MEDIUM] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 2, Metal Framing Systems

Issue: Manufacturer 'Cooper B-Line, Inc.' has been rebranded to 'Eaton B-Line'. The listed company name is outdated.

Action: EDIT

Existing Text: Cooper B-Line, Inc.

Replace With: Eaton B-Line.

5. [MEDIUM] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 3, Examination

Issue: References 'AMCA 201' and 'SMACNA's HVAC Systems - Duct Design' without edition years. Current editions should be specified for clarity.

Action: EDIT

Existing Text: To calculate system effects for air systems, use tables and charts found in AMCA 201, "Fans and Systems," or in SMACNA's "HVAC Systems - Duct Design."

Replace With: To calculate system effects for air systems, use tables and charts found in AMCA 201-22, "Fans and Systems," or in SMACNA's "HVAC Systems - Duct Design," 4th Edition.

Reference: AMCA 201

6. [MEDIUM] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 3, General Procedures for Testing and Balancing

Issue: References ASHRAE 111 and SMACNA TAB standard without edition years. Should specify current editions.

Action: EDIT

Existing Text: Perform testing and balancing procedures on each system according to the procedures contained in AABC's "National Standards for Total System Balance", ASHRAE 111, and SMACNA's "HVAC Systems - Testing, Adjusting, and Balancing" and in this Section.

Replace With: Perform testing and balancing procedures on each system according to the procedures contained in AABC's "National Standards for Total System Balance" (current edition), ASHRAE 111-2008, and SMACNA's "HVAC Systems - Testing, Adjusting, and Balancing," 3rd Edition, and in this Section.

Reference: ASHRAE 111

7. [MEDIUM] 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 3, Duct Label Installation

Issue: References 'ASME A13.1' for hazardous material exhaust without specifying the edition. Current edition is ASME A13.1-2020.

Action: EDIT

Existing Text: ASME A13.1 Colors and Designs:  For hazardous material exhaust.

Replace With: ASME A13.1-2020 Colors and Designs:  For hazardous material exhaust.

Reference: ASME A13.1-2020

8. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 2, Fire-Rated Insulation Systems

Issue: Fire-rated board references ASTM C 656, Type II, Grade 6. This standard covers calcium silicate block and pipe insulation, which may not be appropriate for duct fire-rated assemblies. Verify product compatibility with fire-rated assembly listing.

Action: EDIT

Existing Text: Fire-Rated Board:  Structural-grade, press-molded, xonolite calcium silicate, fireproofing board suitable for operating temperatures up to 1700 deg F.  Comply with ASTM C 656, Type II, Grade 6.

Replace With: Fire-Rated Board:  Structural-grade, press-molded calcium silicate fireproofing board suitable for operating temperatures up to 1700 deg F. Comply with ASTM C656, Type II, and the specific UL or FM fire-rated assembly listing.

Reference: ASTM C656

9. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 3, Penetrations, Insulation Installation at Fire-Rated Wall and Partition Penetrations

Issue: Typo in section reference - 'Firestopping' is misspelled as 'irestopping'.

Action: EDIT

Existing Text: Comply with requirements in Section 078413 "Penetration Firestopping"irestopping and fire-resistive joint sealers.

Replace With: Comply with requirements in Section 078413 "Penetration Firestopping" for firestopping and fire-resistive joint sealers.

10. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 3, General Installation Requirements

Issue: Staple spacing has unresolved bracketed option '[2 inches] [4 inches]' that should have been selected during specification editing.

Action: EDIT

Existing Text: Staple laps with outward clinching staples along edge at [2 inches] [4 inches] o.c.

Replace With: Staple laps with outward clinching staples along edge at 4 inches o.c.

# LOW (6)

1. [LOW] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 1, Definitions

Issue: Specification guide editing note 'Retain definitions remaining after this Section has been edited' was not deleted and remains in the document.

Action: DELETE

Existing Text: Retain definitions remaining after this Section has been edited.

2. [LOW] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, Definitions

Issue: Specification guide editing note 'Retain definition(s) remaining after this Section has been edited' was not deleted.

Action: DELETE

Existing Text: Retain definition(s) remaining after this Section has been edited.

3. [LOW] 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 3, Pipe Label Installation

Issue: Missing space in dimension - '1-1/2 incheshigh' should be '1-1/2 inches high'.

Action: EDIT

Existing Text: Lettering Size:  At least 1-1/2 incheshigh.

Replace With: Lettering Size:  At least 1-1/2 inches high.

4. [LOW] 230713 - DUCT INSULATION.docx

Section: Part 2, Factory-Applied Jackets

Issue: Specification guide note 'Knauf is the only mineral-fiber insulation manufacturer that offers factory-applied FSP jacket...' was not deleted and remains in the document.

Action: DELETE

Existing Text: Knauf is the only mineral-fiber insulation manufacturer that offers factory-applied FSP jacket for blanket insulation.  CertainTeed and Johns Manville offer a vinyl jacket, but it does not comply with ASTM C 1136.  Owens Corning does not offer an FSP or a vinyl product.

5. [LOW] 230719 - HVAC PIPING INSULATION.docx

Section: Part 2, Insulation Materials

Issue: Incomplete editing note 'Pipe insulation wicking system is a patented product offered only by the two manufacturers listed...' left in document without associated product listing.

Action: DELETE

Existing Text: Pipe insulation wicking system is a patented product offered only by the two manufacturers listed.  Product is designed for use on below-ambient temperature (above freezing) services located in severely hot and humid environments.  See Evaluations for additional product information.

6. [LOW] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 3, Final Report, Pump Test Reports

Issue: Editing note 'Net positive suction head is important for pumps in open circuits...' was not deleted from the document.

Action: DELETE

Existing Text: Net positive suction head is important for pumps in open circuits and for pumps handling fluids at elevated temperatures.

# GRIPES (2)

1. [GRIPES] 230529 - HANGERS AND SUPPORTS.docx

Section: Part 3, Hanger and Support Schedule

Issue: The specification lists an exhaustive catalog of MSS hanger types (Types 1 through 58 plus numerous building attachments) when most K-12 mechanical rooms only need a handful of standard hanger types. This level of detail is rarely necessary and adds bulk to the specification without practical benefit.

Action: EDIT

Existing Text: Horizontal-Piping Hangers and Supports:  Unless otherwise indicated and except as specified in piping system Sections, install the following types: [extensive list of MSS Types 1-58]...

Replace With: Consider simplifying to specify only commonly-used hanger types (MSS Types 1, 5, 8, 24) with a general note permitting other MSS SP-58 types as appropriate for specific conditions.

2. [GRIPES] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 3, Final Report

Issue: The final report content requirements span multiple pages of extremely detailed data requirements for every conceivable piece of equipment. For a typical K-12 project with package rooftop units and simple hydronic systems, much of this is overkill and increases TAB costs without proportional benefit.

Action: EDIT

Existing Text: Air-Handling-Unit Test Reports [extensive multi-page requirements]...

Replace With: Consider tailoring report requirements to actual equipment on the project. Simpler systems warrant simpler reports.