# M&P Specification Review Report

Generated: 2025-12-11 11:43
Model: claude-sonnet-4-5-20250929
Files Reviewed: 11

# Files Reviewed

211313 - AUTOMATIC FIRE SPRINKLERS.docx

220517 fl - Sleeves and Sleeve Seals for Plumbing Piping.docx

220518 fl - Escutcheons for Plumbing Piping.docx

220523 fl - General-Duty Valves for Plumbing Piping.docx

220529 fl - Hangers and Supports for Plumbing Piping and Equipment.docx

220553 fl - Identification for Plumbing Piping and Equipment.docx

230529 - HANGERS AND SUPPORTS FOR HVAC PIPING AND EQUIPMENT.docx

230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

230713 - DUCT INSULATION.docx

230719 - HVAC PIPING INSULATION.docx

# Summary

| CRITICAL 12 | HIGH 17 | MEDIUM 19 | LOW 13 | GRIPES 3 | TOTAL 64 |
| --- | --- | --- | --- | --- | --- |

Token Usage: 75,697 input → 15,099 output

Processing Time: 249.8 seconds

# Alerts

## LEED References Detected

The following LEED references were found. Since this is not a LEED project, these should be removed:

230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Line 49: LEED

Line 121: LEED

Line 125: LEED

Line 217: LEED

230713 - DUCT INSULATION.docx

Line 59: LEED

Line 61: LEED

Line 65: LEED

Line 261: LEED

Line 265: LEED

... and 7 more

230719 - HVAC PIPING INSULATION.docx

Line 45: LEED

Line 47: LEED

Line 51: LEED

Line 233: LEED

Line 237: LEED

... and 11 more

# Findings

# CRITICAL (12)

1. [CRITICAL] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 1, GENERAL, Use this Section... statement at top

Issue: Wrong reference to Section 230548.13. The correct format for a vibration controls section in CSI MasterFormat would be Section 230548 (or similar). Also, this cross-reference note should be removed or clarified because DSA jurisdiction requires seismic design in California, making the conditional language inappropriate for a DSA project.

Action: EDIT

Existing Text: Use this Section if Project is in a seismic area.  Use Section 230548.13 "Vibration Controls for HVAC" for Projects not in a seismic area.

Replace With: This Section is for use on Projects subject to DSA seismic design requirements per CBC 2022 and DSA IR A-6.

Reference: CBC 2022, DSA IR A-6

2. [CRITICAL] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 1, DESIGN REQUIREMENTS, First paragraph

Issue: Incorrect edition of NFPA 13. California has adopted NFPA 13, 2022 edition as part of CBC 2022. Verify the correct edition adopted by the state.

Action: EDIT

Existing Text: Wet pipe fire sprinkler system shall conform to NFPA13, 2022 edition.

Replace With: Wet pipe fire sprinkler system shall conform to NFPA 13, 2022 edition, as adopted by CBC 2022.

Reference: CBC 2022

3. [CRITICAL] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 1, REGULATORY REQUIREMENTS

Issue: Missing seismic design and certification requirements for fire sprinkler systems. DSA requires specific seismic design, certification, and submittal documentation per DSA IR A-6.

Action: ADD

Replace With: Seismic Design and Restraint: Design and detail seismic bracing and restraints in accordance with NFPA 13, Chapter 9, and DSA IR A-6. Provide seismic certification by manufacturer or third-party engineer. Submit OSP and OSHPD pre-approval (OPA) where applicable.

Reference: DSA IR A-6, NFPA 13 Chapter 9

4. [CRITICAL] 220517 fl - Sleeves and Sleeve Seals for Plumbing Piping.docx

Section: Part 1, QUALITY ASSURANCE

Issue: References 'SMACNA Seismic Restraint Manual Guidelines for Mechanical Systems' which is primarily for HVAC, not plumbing. For plumbing piping seismic restraint, reference ASCE 7 and CBC Chapter 16, or ASPE standards.

Action: EDIT

Existing Text: SMACNA Seismic Restraint Manual Guidelines for Mechanical Systems.

Replace With: CBC 2022 Chapter 16, ASCE 7-22 Chapter 13, and applicable ASPE standards for seismic design and restraint.

Reference: CBC 2022 Chapter 16, ASCE 7-22

5. [CRITICAL] 220523 fl - General-Duty Valves for Plumbing Piping.docx

Section: Part 1, Related Sections

Issue: References 'Division 15' and 'Division 2' which are outdated CSI MasterFormat divisions. Division 15 was replaced by Division 22 (Plumbing) and Division 23 (HVAC) in MasterFormat 2004. Division 2 is now Division 31 (Earthwork) and Division 33 (Utilities).

Action: EDIT

Existing Text: Related Sections:

Division 2 water distribution piping Sections for general-duty and specialty valves for site construction piping.

Division 15 plumbing piping Sections for specialty valves applicable to those Sections only.

Division 15 Section "Identification for Plumbing Piping and Equipment" for valve tags and schedules.

Replace With: Related Sections:

Division 33 Utilities Sections for general-duty and specialty valves for site utilities piping.

Division 22 Plumbing Sections for specialty valves applicable to those Sections only.

Section 220553 "Identification for Plumbing Piping and Equipment" for valve tags and schedules.

6. [CRITICAL] 220529 fl - Hangers and Supports for Plumbing Piping and Equipment.docx

Section: Part 1, QUALITY ASSURANCE

Issue: References 'SMACNA Seismic Restraint Manual Guidelines for Mechanical Systems' which is primarily for HVAC. For plumbing piping seismic restraint, reference ASCE 7, CBC Chapter 16, and MSS SP-127 or SP-69.

Action: EDIT

Existing Text: SMACNA Seismic Restraint Manual Guidelines for Mechanical Systems.

Replace With: CBC 2022 Chapter 16, ASCE 7-22 Chapter 13, MSS SP-69 'Pipe Hangers and Supports - Selection and Application', and MSS SP-127 'Bracing for Piping Systems Seismic - Wind - Dynamic Design, Selection, and Installation'.

Reference: CBC 2022 Chapter 16, ASCE 7-22, MSS SP-69, MSS SP-127

7. [CRITICAL] 220553 fl - Identification for Plumbing Piping and Equipment.docx

Section: Part 1, QUALITY ASSURANCE

Issue: References 'SMACNA Seismic Restraint Manual Guidelines for Mechanical Systems' in a plumbing identification section, which is not relevant to pipe and equipment identification. This appears to be copied from another section.

Action: DELETE

Existing Text: SMACNA Seismic Restraint Manual Guidelines for Mechanical Systems.

8. [CRITICAL] 230529 - HANGERS AND SUPPORTS FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 1, PERFORMANCE REQUIREMENTS

Issue: States 'Design seismic-restraint hangers and supports for piping and equipment' but does not reference DSA-specific requirements. For California K-12 DSA projects, seismic design must comply with DSA IR A-6 and include certification and pre-approval (OPA) where applicable.

Action: EDIT

Existing Text: Design seismic-restraint hangers and supports for piping and equipment and obtain approval from authorities having jurisdiction.

Replace With: Design seismic-restraint hangers and supports for piping and equipment in accordance with CBC 2022 Chapter 16, ASCE 7-22 Chapter 13, and DSA IR A-6. Obtain DSA approval. Provide seismic certification by manufacturer or third-party engineer. Submit OSHPD pre-approval (OPA) documentation where applicable.

Reference: CBC 2022 Chapter 16, ASCE 7-22, DSA IR A-6

9. [CRITICAL] 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 1, SUMMARY, Section Includes

Issue: Missing section header 'SECTION 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT' at the beginning of the specification. The document starts directly with 'GENERAL'.

Action: ADD

Replace With: SECTION 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT

10. [CRITICAL] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, SUMMARY, Section Includes

Issue: Missing section header 'SECTION 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC' at the beginning of the specification. The document starts directly with 'GENERAL'.

Action: ADD

Replace With: SECTION 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC

11. [CRITICAL] 230713 - DUCT INSULATION.docx

Section: Part 1, SUMMARY, Section Includes

Issue: Missing section header 'SECTION 230713 - DUCT INSULATION' at the beginning of the specification. The document starts directly with 'GENERAL'.

Action: ADD

Replace With: SECTION 230713 - DUCT INSULATION

12. [CRITICAL] 230719 - HVAC PIPING INSULATION.docx

Section: Part 1, SUMMARY, Section Includes

Issue: Missing section header 'SECTION 230719 - HVAC PIPING INSULATION' at the beginning of the specification. The document starts directly with 'GENERAL'.

Action: ADD

Replace With: SECTION 230719 - HVAC PIPING INSULATION

# HIGH (17)

1. [HIGH] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 1, QUALIFICATIONS

Issue: Section refers to 'Uniform Fire Code with California amendments' which is outdated nomenclature. California uses the California Fire Code (CFC) which is based on the International Fire Code (IFC) with California amendments.

Action: EDIT

Existing Text: Code Requirements:  All work covered by this Section shall conform to the 2022 edition of NFPA 13, California State Fire Marshal, DSA, Uniform Fire Code with California amendments.

Replace With: Code Requirements: All work covered by this Section shall conform to the 2022 edition of NFPA 13, California Fire Code (CFC) 2022 with California amendments, California State Fire Marshal requirements, and DSA regulations.

Reference: CFC 2022

2. [HIGH] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 2, Wet Pipe System, Pipe specifications

Issue: ASTM A135 is not an appropriate standard for fire sprinkler pipe. ASTM A53 or ASTM A795 should be used. ASTM A135 is for electric-resistance-welded steel pipe and is typically not approved for fire sprinkler systems.

Action: EDIT

Existing Text: Black Steel, 1"-2", Schedule 40, ASTM A135 or ASTM A795 for all piping with threaded joints and fittings.  Pipe must be UL Listed.

Black Steel 2 ½" -6", Schedule 10, ASTM A135 or ASTM A795 for all piping with grooved joints and fittings.

Replace With: Black Steel, 1"-2", Schedule 40, ASTM A53 or ASTM A795 for all piping with threaded joints and fittings. Pipe must be UL Listed.

Black Steel 2-1/2"-6", Schedule 10 (for grooved systems), ASTM A53 or ASTM A795 for all piping with grooved joints and fittings. Verify Schedule 10 is permitted by manufacturer's listing for grooved applications.

Reference: NFPA 13, Section 6.3

3. [HIGH] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 2, Sprinkler Heads, third paragraph

Issue: Inconsistent temperature ratings. The specification states sprinklers in areas experiencing over 100°F shall be 200-225°F rated, and boiler rooms shall be 250-290°F. This may be inadequate. NFPA 13 requires consideration of ambient plus 20°F for intermediate temperature (typically 155°F-200°F) or ambient plus 50°F for ordinary temperature (135°F-170°F). Verify these ratings meet NFPA 13 Table 6.2.5.1.

Action: EDIT

Existing Text: Sprinklers in concealed spaces, exterior locations and any other areas which may experience over 100 degrees F ambient temperatures shall be furnished with 200 to 225 degree rated sprinklers.  Sprinkler heads in boiler rooms shall be furnished with sprinklers rated at 250 to 290 degrees F.

Replace With: Sprinkler temperature ratings shall be selected in accordance with NFPA 13, Table 6.2.5.1, based on maximum anticipated ceiling temperatures. Sprinklers in concealed spaces, exterior locations, and areas that may experience elevated ambient temperatures shall have temperature ratings a minimum of 50°F above maximum anticipated ceiling temperature. Coordinate ratings with design conditions and obtain approval prior to procurement.

Reference: NFPA 13, Section 6.2.5 and Table 6.2.5.1

4. [HIGH] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 2, Sprinkler Heads

Issue: Specification prohibits extended coverage heads without technical justification. Extended coverage heads are allowed by NFPA 13 and may be more efficient. This appears to be an arbitrary restriction.

Action: EDIT

Existing Text: Sprinkler heads in light hazard occupancy shall be quick response type.  Sprinklers shall be same manufacturer throughout.  Extended coverage heads will not be permitted.

Replace With: Sprinkler heads in light hazard occupancy shall be quick response type per NFPA 13, Section 6.2.3.2. Sprinklers shall be same manufacturer throughout to extent practical. Extended coverage heads are permitted if approved by Architect and authorities having jurisdiction, and if hydraulic calculations demonstrate compliance with NFPA 13.

Reference: NFPA 13, Section 6.2.3.2

5. [HIGH] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 3, INSTALLATION, Underground piping paragraph

Issue: 36-inch minimum bury depth may not be adequate for freeze protection in all California climates, and conflicts with typical depth requirements for fire service. Verify this meets local frost depth and fire service requirements.

Action: EDIT

Existing Text: Underground piping shall have a 36" minimum bury.  Pipe shall be installed on a flat undisturbed sand bed.

Replace With: Underground piping burial depth shall be a minimum of 36 inches or below frost line and shall comply with NFPA 24 requirements for the local climate zone. Where site conditions or frost depth require greater depth, increase burial accordingly. Pipe shall be installed on a flat undisturbed sand bed.

Reference: NFPA 24, Section 10.6

6. [HIGH] 220517 fl - Sleeves and Sleeve Seals for Plumbing Piping.docx

Section: Part 1, QUALITY ASSURANCE, Code Requirements

Issue: References '2022 California Plumbing Code' which is correct, but should clarify that this is C.C.R., Title 24, Part 5 (already listed) to avoid redundancy and confusion.

Action: EDIT

Existing Text: C.C.R., Title 24, Part 5 (2022 CPC).

2022 California Plumbing Code.

Replace With: C.C.R., Title 24, Part 5 (2022 California Plumbing Code).

Reference: CPC 2022

7. [HIGH] 220523 fl - General-Duty Valves for Plumbing Piping.docx

Section: Part 1, QUALITY ASSURANCE

Issue: References 'SMACNA Seismic Restraint Manual Guidelines for Mechanical Systems' which is primarily for HVAC, not plumbing valves. For plumbing piping seismic restraint, reference ASCE 7 and CBC Chapter 16.

Action: EDIT

Existing Text: SMACNA Seismic Restraint Manual Guidelines for Mechanical Systems.

Replace With: CBC 2022 Chapter 16 and ASCE 7-22 Chapter 13 for seismic design and restraint.

Reference: CBC 2022 Chapter 16, ASCE 7-22

8. [HIGH] 220523 fl - General-Duty Valves for Plumbing Piping.docx

Section: Part 2, GENERAL REQUIREMENTS FOR VALVES, Extended stems paragraph

Issue: Extended stem requirement for insulated piping specifies '2" extended handles' but does not clarify whether this is the extension beyond the insulation surface or total handle length. Clarify dimension for constructability.

Action: EDIT

Existing Text: Extended stems: Where piping insulation is indicated or specified, valves shall be equipped with 2" extended handles of non-thermal conductive material.

Replace With: Extended Stems: Where piping insulation is indicated or specified, valves shall be equipped with extended handles of non-thermal conductive material, with handle extension sufficient to project a minimum of 2 inches beyond insulation and jacket surface.

9. [HIGH] 220529 fl - Hangers and Supports for Plumbing Piping and Equipment.docx

Section: Part 2, Pipe Supports, General description

Issue: Specification references hanger spacing per '2022 California Plumbing Code Table 313.1' but should verify this table reference is correct and whether it applies to all services (hot, cold, waste, etc.).

Action: EDIT

Existing Text: Hanger spacing and location shall conform to 2022 California Plumbing Code Table 313.1.

Replace With: Hanger spacing and location shall conform to CPC 2022 Table 313.1 for plumbing piping. For piping not covered by CPC Table 313.1, comply with MSS SP-69 'Pipe Hangers and Supports - Selection and Application'.

Reference: CPC 2022 Table 313.1, MSS SP-69

10. [HIGH] 220529 fl - Hangers and Supports for Plumbing Piping and Equipment.docx

Section: Part 2, Pipe Supports, Lateral bracing paragraph

Issue: References 'SMACNA "Guidelines for Seismic Restraints of Piping Systems"' which is an HVAC-focused document. For plumbing, should reference MSS SP-127 or CBC Chapter 16 requirements.

Action: EDIT

Existing Text: Provide lateral bracing as manufactured by B-Line or approved equal for all piping to prevent swaying or movement in accordance with SMACNA "Guidelines for Seismic Restraints of Piping Systems".

Replace With: Provide lateral bracing as manufactured by B-Line, Tolco, or approved equal for all piping to prevent swaying or movement in accordance with CBC 2022 Chapter 16, ASCE 7-22 Chapter 13, and MSS SP-127. Design seismic restraints for DSA requirements per DSA IR A-6.

Reference: CBC 2022 Chapter 16, ASCE 7-22, MSS SP-127, DSA IR A-6

11. [HIGH] 230529 - HANGERS AND SUPPORTS FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 1, Related Sections

Issue: References 'Section 230548 "Vibration and Seismic Controls for HVAC"' but does not clarify whether vibration isolation is included in that section or this section. For DSA projects, seismic restraint of isolated equipment requires special detailing.

Action: EDIT

Existing Text: Section 230548 "Vibration and Seismic Controls for HVAC for vibration isolation devices.

Replace With: Section 230548 "Vibration and Seismic Controls for HVAC" for vibration isolation devices and seismic restraint of vibration-isolated equipment. Coordinate seismic restraint details with requirements in this Section.

12. [HIGH] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, ACTION SUBMITTALS, LEED Submittals

Issue: References 'ASHRAE/IESNA 90.1' which is outdated nomenclature. The current standard is 'ANSI/ASHRAE/IES Standard 90.1'. Also, verify the correct edition year for the project (2022 California Energy Code references ASHRAE 90.1-2019).

Action: EDIT

Existing Text: TAB Report for Prerequisite EA 2:  Documentation of work performed for ASHRAE/IESNA 90.1, Section 6.7.2.3 - "System Balancing."

Replace With: TAB Report for Prerequisite EA 2: Documentation of work performed demonstrating compliance with ANSI/ASHRAE/IES Standard 90.1-2019, Section 6.7.2.3 - "System Balancing," as required by California Energy Code 2022.

Reference: California Energy Code 2022, ANSI/ASHRAE/IES 90.1-2019

13. [HIGH] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, INFORMATIONAL SUBMITTALS

Issue: Contract Documents examination report is required 'Within 30 days of Contractor's Notice to Proceed' but for DSA projects, this should be coordinated with DSA submittal and approval timelines which may differ from standard AIA timelines.

Action: EDIT

Existing Text: Contract Documents Examination Report:  Within 30 days of Contractor's Notice to Proceed, submit the Contract Documents review report as specified in Part 3.

Replace With: Contract Documents Examination Report: Within 30 days of Contractor's Notice to Proceed, or prior to start of TAB work, whichever is earlier, submit the Contract Documents review report as specified in Part 3. Coordinate timing with DSA submittal requirements and overall project schedule.

14. [HIGH] 230713 - DUCT INSULATION.docx

Section: Part 1, ACTION SUBMITTALS, LEED Submittals

Issue: LEED submittal requirements reference VOC limits and California Department of Health Services testing, but do not reference the current applicable standard. For adhesives and sealants in California, reference California SCAQMD Rule 1168 and current CDPH Standard Method V1.2 (previously called 'Section 01350').

Action: EDIT

Existing Text: Laboratory Test Reports for Credit IEQ 4:  For adhesives and sealants, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Replace With: Laboratory Test Reports for Credit IEQ 4: For adhesives and sealants, documentation indicating that products comply with CDPH Standard Method V1.2 (formerly Section 01350) for low-emitting materials, and California SCAQMD Rule 1168 VOC limits where applicable.

Reference: CDPH Standard Method V1.2, SCAQMD Rule 1168

15. [HIGH] 230713 - DUCT INSULATION.docx

Section: Part 2, INSULATION MATERIALS, Mineral-Fiber Blanket

Issue: Specifies ASTM C 1290, Type III for blanket insulation with FSK jacket, but should verify this type designation is current and appropriate for all duct applications listed in the schedules. Type III is for flexible duct wrap; verify if rigid board is needed for any applications.

Action: EDIT

Existing Text: Mineral-Fiber Blanket Insulation:  Mineral or glass fibers bonded with a thermosetting resin.  Comply with ASTM C 553, Type II and ASTM C 1290, Type III with factory-applied FSK jacket.

Replace With: Mineral-Fiber Blanket Insulation: Mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C 553, Type II (for temperatures up to 250°F) and ASTM C 1290, Type III (for flexible duct wrap with factory-applied FSK jacket). For higher temperature applications, use board insulation per ASTM C 612.

Reference: ASTM C 553, ASTM C 1290, ASTM C 612

16. [HIGH] 230719 - HVAC PIPING INSULATION.docx

Section: Part 1, ACTION SUBMITTALS, LEED Submittals

Issue: LEED submittal requirements reference VOC limits and California Department of Health Services testing using outdated terminology. Should reference current CDPH Standard Method V1.2.

Action: EDIT

Existing Text: Laboratory Test Reports for Credit IEQ 4:  For adhesives and sealants, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Replace With: Laboratory Test Reports for Credit IEQ 4: For adhesives and sealants, documentation indicating that products comply with CDPH Standard Method V1.2 for low-emitting materials testing.

Reference: CDPH Standard Method V1.2

17. [HIGH] 230719 - HVAC PIPING INSULATION.docx

Section: Part 3, INDOOR PIPING INSULATION SCHEDULE, Chilled Water

Issue: Insulation schedule for chilled water specifies 'Mineral-Fiber, Preformed Pipe, Type I: 1 inch thick' but does not verify this thickness meets condensation control requirements or California Energy Code minimum R-value requirements for the climate zone.

Action: EDIT

Existing Text: Chilled Water:

Insulation shall be the following:

Mineral-Fiber, Preformed Pipe, Type I:  1 inch thick.

Replace With: Chilled Water:

Insulation shall be the following:

Mineral-Fiber, Preformed Pipe, Type I: Minimum 1 inch thick, or thickness required to meet California Energy Code 2022 minimum R-value per Table 120.3 and to prevent condensation under design conditions, whichever is greater. Verify thickness with condensation control calculations.

Reference: California Energy Code 2022, Section 120.3 and Table 120.3

# MEDIUM (19)

1. [MEDIUM] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 1, Manufacture's Data

Issue: Typo in heading: 'Manufacture's' should be 'Manufacturer's'.

Action: EDIT

Existing Text: Manufacture's Data

Replace With: Manufacturer's Data

2. [MEDIUM] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 1, QUALIFICATIONS, Retain terms... paragraph

Issue: Contains unedited boilerplate instruction text that should be removed before issuing specifications.

Action: DELETE

Existing Text: Retain terms that remain after this Section has been edited for a project.

3. [MEDIUM] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 1, Drawings and Hydraulic calculations

Issue: Specifying AutoCAD 2019 as 'the latest' is outdated. AutoCAD 2019 was released in 2018. Specify current version or allow for compatibility with current software.

Action: EDIT

Existing Text: Drawings shall be made in AutoCAD 2019 version as the latest.  Drawings shall be same size as contract drawings.

Replace With: Drawings shall be made in AutoCAD (version 2019 or later) in DWG format compatible with current Architect's software. Drawings shall be same size as contract drawings.

4. [MEDIUM] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 2, REQUIRMENTS

Issue: Section heading misspelled: 'REQUIRMENTS' should be 'REQUIREMENTS'.

Action: EDIT

Existing Text: REQUIRMENTS

Replace With: REQUIREMENTS

5. [MEDIUM] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 2, REQUIRMENTS section, multiple locations

Issue: Contains multiple instances of unedited boilerplate instruction text (e.g., 'Copy "Elastomeric Isolation Pads" Paragraph below...', 'Coordinate specifications for products...', 'Verify availability of various pad materials...'). This editorial instruction text should be removed.

Action: DELETE

Existing Text: Copy "Elastomeric Isolation Pads" Paragraph below and re-edit for each product...Coordinate specifications for products in this Section with structural engineer...Copy "Sandwich-Core Material" Subparagraph below...

6. [MEDIUM] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 2, MATERIALS, ACCESS PANELS

Issue: ACCESS PANELS section is misplaced in a fire sprinkler specification and appears to be copied from a different section. Fire sprinkler specs would require fire sprinkler access panels, but this describes general access panels. Remove or clarify.

Action: DELETE

Existing Text: ACCESS PANELS

Square, stainless steel, with vandal proof door lock operated by allen wrench: Manufacturer's:  Smith – 4760, Elmdor – DW-AKL

7. [MEDIUM] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 3, INSTALLATION, Drainage paragraph

Issue: References 'CBC standards' which is non-specific. Should reference specific code sections or NFPA 13 requirements for drainage.

Action: EDIT

Existing Text: Sprinkler system shall be provided with complete drainage facilities in accordance with CBC standards.

Replace With: Sprinkler system shall be provided with complete drainage facilities in accordance with NFPA 13, Section 8.17, and CBC Chapter 9.

Reference: NFPA 13, Section 8.17; CBC 2022 Chapter 9

8. [MEDIUM] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 3, INSTALLATION, Testing paragraph

Issue: Reference to 'CBC standards' for testing is non-specific. Should reference NFPA 13 Chapter 11 for system acceptance testing.

Action: EDIT

Existing Text: Upon completion of work and before substantial completion, subject entire system, including underground piping, to tests as required by NFPA13 and CBC standards and furnish Owner with a certificate of compliance as required.

Replace With: Upon completion of work and before substantial completion, subject entire system, including underground piping, to hydrostatic and operational acceptance tests as required by NFPA 13, Chapter 11. Furnish Owner with test reports and certificate of compliance signed by contractor and approved by authority having jurisdiction.

Reference: NFPA 13, Chapter 11

9. [MEDIUM] 220517 fl - Sleeves and Sleeve Seals for Plumbing Piping.docx

Section: Part 2, GROUT

Issue: ASTM C 1107 is correct but the grade designation is incomplete. Should specify 'Grade B, post-hardening and volume-adjusting' more clearly and indicate suitable applications.

Action: EDIT

Existing Text: Standard:  ASTM C 1107/C 1107M, Grade B, post-hardening and volume-adjusting, dry, hydraulic-cement grout.

Replace With: Standard: ASTM C 1107/C 1107M, Grade B (flowable consistency), post-hardening and volume-adjusting, dry, hydraulic-cement grout suitable for interior and exterior applications.

Reference: ASTM C 1107

10. [MEDIUM] 220523 fl - General-Duty Valves for Plumbing Piping.docx

Section: Part 2, GENERAL REQUIREMENTS FOR VALVES, Bronze valves paragraph

Issue: Specification states 'Bronze valves shall be made with dezincification-resistant material' twice in the same article (in general requirements and again later). Redundant text should be consolidated.

Action: EDIT

Existing Text: Bronze valves shall be made with dezincification-resistant material. [later repeated]

Replace With: Consolidate to single statement: 'Bronze valves shall be made with dezincification-resistant materials per ASTM B 98 or ASTM B 584, alloys C87850 or equivalent. This includes body, ball, stem, and trim where applicable.'

11. [MEDIUM] 220523 fl - General-Duty Valves for Plumbing Piping.docx

Section: Part 2, BRONZE BALL VALVES, Description

Issue: Specification prohibits 'threaded stem designs' for ball valves but does not provide technical justification. Threaded stem designs are common and acceptable for many applications. Verify this restriction is necessary.

Action: EDIT

Existing Text: Body Design:  Three piece with threaded body packnut design (no threaded stem designs allowed) with adjustable stem packing.

Replace With: Body Design: Three piece with threaded body and union-end or flanged construction, with adjustable stem packing. Threaded-stem designs are not permitted.

12. [MEDIUM] 220529 fl - Hangers and Supports for Plumbing Piping and Equipment.docx

Section: Part 2, Hanger Rods and Spacing table

Issue: Hanger rod spacing table may not be adequate for all piping services and weights. CPC Table 313.1 provides more detailed requirements by pipe material and service. Verify this simplified table is appropriate.

Action: EDIT

Existing Text: Hanger Rods and Spacing shall conform to the following table:

Pipe Sizes				Spacing			Rods
2 Inch and Smaller		6 Feet			3/8 Inch
2-1/2 Inch to 3 Inch		8 Feet			1/2 Inch
4 Inch and larger			8 Feet			5/8 Inch

Replace With: Hanger rod sizing and spacing shall conform to CPC 2022 Table 313.1 for plumbing piping. For piping not covered by CPC Table 313.1, comply with MSS SP-69. As a minimum, provide:

Pipe Sizes 2 inches and smaller: Maximum 6-foot spacing, 3/8-inch rods
Pipe Sizes 2-1/2 inches to 3 inches: Maximum 8-foot spacing, 1/2-inch rods
Pipe Sizes 4 inches and larger: Maximum 8-foot spacing, 5/8-inch rods (minimum)

Reduce spacing near valves, fittings, and concentrated loads.

Reference: CPC 2022 Table 313.1, MSS SP-69

13. [MEDIUM] 220553 fl - Identification for Plumbing Piping and Equipment.docx

Section: Part 2, PIPE LABELS

Issue: Specifies lettering size of 'At least 1-1/2 inches high' which may be excessive for small piping. ASME A13.1 provides guidance on letter size based on pipe diameter. Verify this requirement is appropriate for all pipe sizes.

Action: EDIT

Existing Text: Lettering Size:  At least 1-1/2 incheshigh.

Replace With: Lettering Size: Minimum letter size shall be in accordance with ASME A13.1, based on pipe outside diameter:
- Pipe 3/4" to 1-1/4": 1/2" letters
- Pipe 1-1/2" to 2": 3/4" letters  
- Pipe 2-1/2" to 6": 1-1/4" letters
- Pipe 8" and larger: 2-1/2" letters minimum

Reference: ASME A13.1

14. [MEDIUM] 230529 - HANGERS AND SUPPORTS FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 1, ACTION SUBMITTALS, Shop Drawings

Issue: Requires shop drawings to be 'Signed and sealed by a qualified professional engineer' but does not clarify that for DSA projects, the engineer must be licensed in California and familiar with DSA requirements.

Action: EDIT

Existing Text: Shop Drawings:  Signed and sealed by a qualified professional engineer.

Replace With: Shop Drawings: Signed and sealed by a professional engineer licensed in the State of California and experienced with DSA seismic design requirements.

Reference: California Business and Professions Code, DSA requirements

15. [MEDIUM] 230553 - IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 2, DUCT LABELS

Issue: Specifies lettering size of 'At least 1-1/2 inches high' which may be excessive for small ducts. Consider providing guidance based on duct size for better proportionality.

Action: EDIT

Existing Text: Lettering Size:  At least 1-1/2 inches high.

Replace With: Lettering Size: Minimum letter size based on duct size:
- Ducts less than 12" wide: 1/2" letters
- Ducts 12" to 24" wide: 1" letters
- Ducts over 24" wide: 1-1/2" letters minimum

16. [MEDIUM] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 1, QUALITY ASSURANCE, ASHRAE/IESNA Compliance

Issue: References 'ASHRAE/IESNA 90.1' which should be updated to 'ANSI/ASHRAE/IES 90.1-2019' to match the edition adopted by California Energy Code 2022.

Action: EDIT

Existing Text: ASHRAE/IESNA Compliance:  Applicable requirements in ASHRAE/IESNA 90.1, Section 6.7.2.3 - "System Balancing."

Replace With: Energy Code Compliance: Applicable requirements in ANSI/ASHRAE/IES Standard 90.1-2019, Section 6.7.2.3 - "System Balancing," as required by California Energy Code 2022, Title 24, Part 6.

Reference: California Energy Code 2022, ANSI/ASHRAE/IES 90.1-2019

17. [MEDIUM] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Part 3, EXAMINATION, Ceiling plenums paragraph

Issue: References 'Section 233113 "Metal Ducts"' for plenum leakage requirements, but does not clarify that for California projects under Title 24, duct and plenum sealing must meet specific leakage class requirements per Section 120.2(d).

Action: EDIT

Existing Text: Examine ceiling plenums and underfloor air plenums used for supply, return, or relief air to verify that they meet the leakage class of connected ducts as specified in Section 233113 "Metal Ducts" and are properly separated from adjacent areas.

Replace With: Examine ceiling plenums and underfloor air plenums used for supply, return, or relief air to verify that they meet the leakage class of connected ducts as specified in Section 233113 "Metal Ducts" and comply with California Energy Code 2022 Section 120.2(d) duct sealing requirements. Verify plenums are properly separated from adjacent areas and that penetrations are sealed and fire-stopped where required.

Reference: California Energy Code 2022, Section 120.2(d)

18. [MEDIUM] 230713 - DUCT INSULATION.docx

Section: Part 3, INDOOR DUCT AND PLENUM INSULATION SCHEDULE

Issue: Schedule specifies 'Internally lined per Section 233113 "Metal Ducts"' for exposed ducts but does not clarify minimum R-value or thickness required to meet California Energy Code 2022. Energy Code Section 120.2 specifies minimum duct insulation R-values.

Action: EDIT

Existing Text: Exposed, supply-air duct and plenum insulation shall be the following:

Internally lined per Section 233113 "Metal Ducts."

Replace With: Exposed, supply-air duct and plenum insulation shall be the following:

Internally lined per Section 233113 "Metal Ducts" with minimum R-value complying with California Energy Code 2022, Section 120.2 and Tables 120.2-A through 120.2-C as applicable for the climate zone and duct location.

Reference: California Energy Code 2022, Section 120.2

19. [MEDIUM] 230719 - HVAC PIPING INSULATION.docx

Section: Part 3, INDOOR PIPING INSULATION SCHEDULE, Heating-Hot-Water

Issue: Heating hot water piping insulation thickness of 2 inches should be verified to comply with California Energy Code requirements, which vary by pipe size and fluid temperature. Table 120.3 provides minimum requirements.

Action: EDIT

Existing Text: Heating-Hot-Water Supply and Return:

Insulation shall be the following:

Mineral-Fiber, Preformed Pipe, Type I: 2 inches thick.

Replace With: Heating-Hot-Water Supply and Return:

Insulation shall be the following:

Mineral-Fiber, Preformed Pipe, Type I: Minimum thickness per California Energy Code 2022, Table 120.3, based on pipe size and fluid operating temperature. Minimum 2 inches for typical applications; verify compliance for all pipe sizes.

Reference: California Energy Code 2022, Section 120.3 and Table 120.3

# LOW (13)

1. [LOW] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 1, SECTION INCLUDES, third paragraph

Issue: Run-on sentence with inconsistent punctuation. Should be broken into clearer statements or use proper list formatting.

Action: EDIT

Existing Text: Work or equipment not indicated or specified which is necessary for the complete and proper operation of the work of the Section in accordance with the true intent and meaning of the contract documents shall be provided by this contractor and incorporated under this Section of the work at no additional cost.

Replace With: Work or equipment not indicated or specified but necessary for the complete and proper operation of the fire sprinkler system in accordance with the true intent and meaning of the contract documents shall be provided by this Contractor and incorporated under this Section at no additional cost to the Owner.

2. [LOW] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 2, Sprinkler Heads, paragraph about escutcheons

Issue: Inconsistent formatting: '=ceilings' contains a stray equals sign.

Action: EDIT

Existing Text: Exposed pipe through walls and =ceilings shall have split ring chrome escutcheon.

Replace With: Exposed pipe through walls and ceilings shall have split ring chrome escutcheon.

3. [LOW] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 3, EXAMINATION, first paragraph

Issue: Inconsistent capitalization and terminology. 'Contractor' should be lowercase when used generically, and 'he' should be 'Contractor' or 'they' for consistency and inclusivity.

Action: EDIT

Existing Text: Contractor shall make a careful examination of the premises and shall thoroughly familiarize themselves with the requirements of the contract.  By submitting a proposal for the work under this section of the specification, the Contractor shall be deemed to have made such a study and the he is familiar with and accepts all conditions of the site.

Replace With: Contractor shall make a careful examination of the premises and shall thoroughly familiarize themselves with the requirements of the Contract. By submitting a proposal for the Work under this Section, the Contractor shall be deemed to have made such a study and to be familiar with and to accept all conditions of the site.

4. [LOW] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Throughout document

Issue: Inconsistent capitalization of 'contractor' vs 'Contractor', 'architect' vs 'Architect', 'owner' vs 'Owner', and 'section' vs 'Section'. CSI format typically capitalizes these terms when referring to specific Contract parties or document divisions.

Action: EDIT

Existing Text: Multiple instances throughout (applies throughout this section)

Replace With: Standardize capitalization: Use 'Contractor', 'Architect', 'Owner', 'Engineer', 'Contract', 'Section', 'Work' when referring to specific Contract parties or Contract Document divisions.

5. [LOW] 220517 fl - Sleeves and Sleeve Seals for Plumbing Piping.docx

Section: Part 1, SUMMARY, Related Documents

Issue: Standard boilerplate includes reference to 'General and Supplementary Conditions and Division 01 Specification Sections'. On DSA projects, 'General Conditions' should reference DSA's required General Conditions (typically based on AIA but with DSA modifications).

Action: EDIT

Existing Text: Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

Replace With: Drawings and general provisions of the Contract, including General Conditions (DSA Form 101), Supplementary Conditions, and Division 01 Specification Sections, apply to this Section.

6. [LOW] 220517 fl - Sleeves and Sleeve Seals for Plumbing Piping.docx

Section: Throughout document

Issue: Inconsistent capitalization and hyphenation: 'blueline prints' vs standard terminology, inconsistent use of hyphens in compound modifiers.

Action: EDIT

Existing Text: Multiple instances (applies throughout this section)

Replace With: Standardize terminology: use 'record drawings' or 'as-built drawings' instead of 'blueline prints'; use consistent hyphenation for compound modifiers (e.g., 'as-built information').

7. [LOW] 220523 fl - General-Duty Valves for Plumbing Piping.docx

Section: Part 1, DEFINITIONS

Issue: Contains instruction text 'Retain definition(s) remaining after this Section has been edited.' which should be removed from final specifications.

Action: DELETE

Existing Text: Retain definition(s) remaining after this Section has been edited.

8. [LOW] 220529 fl - Hangers and Supports for Plumbing Piping and Equipment.docx

Section: Throughout document

Issue: Contains multiple instances of unedited boilerplate instruction text related to painting and touchup that may not apply to plumbing installations or should be coordinated with other sections.

Action: EDIT

Existing Text: Multiple painting-related instruction paragraphs (applies throughout Execution article)

Replace With: Review and coordinate painting and finishing requirements with Division 09 Painting Sections. Remove instruction text or replace with project-specific requirements.

9. [LOW] 220553 fl - Identification for Plumbing Piping and Equipment.docx

Section: Part 1, ACTION SUBMITTALS

Issue: Lists multiple submittal items but does not specify number of copies or submission format (electronic vs. hard copy). For DSA projects, electronic submittals via DSA's ePSSI system are typically required.

Action: ADD

Replace With: Submit all product data, samples, and schedules electronically through DSA's ePSSI system in accordance with DSA procedures. Provide [ ] hard copies of schedules for Architect's review.

Reference: DSA ePSSI requirements

10. [LOW] 230529 - HANGERS AND SUPPORTS FOR HVAC PIPING AND EQUIPMENT.docx

Section: Part 1, DEFINITIONS

Issue: Contains instruction text 'Retain definitions remaining after this Section has been edited.' which should be removed from final specifications.

Action: DELETE

Existing Text: Retain definitions remaining after this Section has been edited.

11. [LOW] 230593 - TESTING, ADJUSTING, AND BALANCING FOR HVAC.docx

Section: Throughout document

Issue: Contains multiple bracketed placeholders such as '[Architect]', '[Owner]', '[Construction Manager]', '[Commissioning Authority]' that should be filled in with the actual party responsible for TAB oversight on this project.

Action: EDIT

Existing Text: Multiple instances of bracketed placeholders (applies throughout)

Replace With: Replace bracketed placeholders with the actual party name responsible for TAB oversight, coordination, and approval on this DSA project.

12. [LOW] 230713 - DUCT INSULATION.docx

Section: Throughout document

Issue: Contains multiple instances of instruction text for spec writers (e.g., 'Retain definition(s) remaining...', 'Revise first subparagraph...', etc.) that should be removed from final specifications.

Action: DELETE

Existing Text: Multiple instances of spec writer instruction text (applies throughout)

13. [LOW] 230719 - HVAC PIPING INSULATION.docx

Section: Throughout document

Issue: Contains extensive instruction text and commentary for spec writers (shown in italics and in notes) that should be removed from final specifications for bidding and construction.

Action: DELETE

Existing Text: Multiple instances of instruction text and spec writer guidance (applies throughout)

# GRIPES (3)

1. [GRIPES] 220517 fl - Sleeves and Sleeve Seals for Plumbing Piping.docx

Section: Part 1, Multiple locations in general coordination articles

Issue: Excessively prescriptive language about contractor coordination and examination of premises. Phrases like 'By the act of submitting a proposal for the work included in this contract, the Contractor shall be deemed to have made such study and examination...' are standard risk-shifting boilerplate but are repetitive across multiple sections and may be viewed as unnecessarily legalistic.

Action: EDIT

Existing Text: Multiple paragraphs about examination, coordination, protection (applies throughout General articles)

Replace With: Consider consolidating repetitive coordination and examination requirements into Division 01 General Requirements rather than repeating in every specification section. This would streamline the specifications.

2. [GRIPES] 220523 fl - General-Duty Valves for Plumbing Piping.docx

Section: Part 1, SUBMITTAL DATA, Substitution Requirements

Issue: The substitution requirements are extremely detailed and rigid ('only one proposed alternate will be considered', extensive documentation requirements, etc.). While thoroughness is good, this level of restriction may discourage competitive bidding and limit contractor flexibility in a supply chain with potential availability issues.

Action: EDIT

Existing Text: Extensive substitution requirements including detailed data requirements and 'No more than one proposed alternate will be considered for each item'

Replace With: Consider simplifying substitution requirements to focus on performance criteria and allow reasonable flexibility for equal products, especially given current supply chain challenges. The current language may unnecessarily limit competition.

3. [GRIPES] 211313 - AUTOMATIC FIRE SPRINKLERS.docx

Section: Part 2, Sprinkler Heads, Alignment requirement

Issue: Requires sprinklers to be 'installed in center of tile at 12" increments from tile edge and shall be aligned with other ceiling mounted devices.' This is an aesthetic requirement that may conflict with hydraulic design requirements or structural conditions and could drive up costs unnecessarily. While desirable, making this mandatory without allowing for field conditions seems overly restrictive.

Action: EDIT

Existing Text: Sprinklers shall be installed in center of tile at 12" increments from tile edge and shall be aligned with other ceiling mounted devices.

Replace With: Consider revising to: 'Sprinklers shall be located to align with ceiling tile grid and other ceiling-mounted devices where practical and where such alignment does not conflict with coverage requirements, structural conditions, or hydraulic design. Coordinate final locations with Architect.'